## CALCULATOR
Panduit Patch Cord Approximate Diameters
[7 empty] | Cat. | AWG | in. |  | mm
[7 empty] | 5e | 24 | 0.215 |  | 5.461
[7 empty] | 6 | 28 | 0.15 |  | 3.81
Enter the cable diameter below and select in. or mm. | [6 empty] | 6 | 24 | 0.235 |  | 5.969
[7 empty] | 6A | 28 | 0.185 |  | 4.699
Cable Diameter = | 0.185 | 1 |  |  |  |  | 6A | 24 | 0.275 |  | 6.985
| Duplex Cable? | 1
Product Family | Part Number | Description | Cable Manager Area |  |  | Recommended Cable Fill (30%) |  |  |  | Maximum Cable Fill (50%)
|  |  | Front Usable Area (sq. in.) | Rear Usable Area (sq. in.) | Total Usable Area (sq. in.) | Front | Rear | Total |  | Front | Rear | Total
PR2V PatchRunner™ 2 Vertical Cable Managers | PR2VD06 | 6" wide | 45.11 | 27.26 | 72.37 | 503 | 304 | 807 |  | 839 | 507 | 1346
| PR2VFD06 | 6" wide, front only | 45.11 | 0 | 45.11 | 503 | 0 | 503 |  | 839 | 0 | 839
| PR2VD08 | 8" wide | 63.71 | 39.73 | 103.44 | 711 | 443 | 1154 |  | 1185 | 739 | 1924
| PR2VFD08 | 8" wide, front only | 63.71 | 0 | 63.71 | 711 | 0 | 711 |  | 1185 | 0 | 1185
| PR2VD10 | 10" wide | 82.31 | 52.21 | 134.52 | 918 | 582 | 1501 |  | 1531 | 971 | 2502
| PR2VFD10 | 10" wide, front only | 82.31 | 0 | 82.31 | 918 | 0 | 918 |  | 1531 | 0 | 1531
| PR2VD12 | 12" wide | 100.9 | 64.68 | 165.58 | 1126 | 721 | 1847 |  | 1876 | 1203 | 3079
| PR2VFD12 | 12" wide, front only | 100.9 | 0 | 100.9 | 1126 | 0 | 1126 |  | 1876 | 0 | 1876
| Single PR2V Finger |  |  |  | 5.8 | 64 |  |  |  | 107
PRV PatchRunner™ Vertical Cable Managers | PRV6 | 6" wide | 38.5 | 26.6 | 65.1 | 429 | 296 | 726 |  | 716 | 494 | 1210
| PRVF6 | 6" wide, front only | 38.5 | 0 | 38.5 | 429 | 0 | 429 |  | 716 | 0 | 716
| PRV8 | 8" wide | 55.3 | 37.7 | 93 | 617 | 420 | 1037 |  | 1028 | 701 | 1729
| PRVF8 | 8" wide, front only | 55.3 | 0 | 55.3 | 617 | 0 | 617 |  | 1028 | 0 | 1028
| PRV10 | 10" wide | 72 | 48.8 | 120.8 | 803 | 544 | 1348 |  | 1339 | 907 | 2247
| PRVF10 | 10" wide, front only | 72 | 0 | 72 | 803 | 0 | 803 |  | 1339 | 0 | 1339
| PRV12 | 12" wide | 88.8 | 59.9 | 148.7 | 991 | 668 | 1659 |  | 1651 | 1114 | 2765
| PRVF12 | 12" wide, front only | 88.8 | 0 | 88.8 | 991 | 0 | 991 |  | 1651 | 0 | 1651
| PRV15 | 15" wide | 113.9 | 76.5 | 190.4 | 1271 | 853 | 2124 |  | 2118 | 1422 | 3541
| PRVF15 | 15" wide, front only | 113.9 | 0 | 113.9 | 1271 | 0 | 1271 |  | 2118 | 0 | 2118
| Single PRV Finger |  |  |  | 4.7 | 52 |  |  |  | 87
Note: Door brackets and cable slack spools reduce cable capacity.
PEV PatchRunner™ High Capacity Vertical Cable Managers | PEV6 | 6" wide | 67.1 | 45.9 | 113 | 748 | 512 | 1261 |  | 1248 | 853 | 2101
| PEVF6 | 6" wide, front only | 67.1 | 0 | 67.1 | 748 | 0 | 748 |  | 1248 | 0 | 1248
| PEV8 | 8" wide | 92.8 | 64.3 | 157.1 | 1035 | 717 | 1753 |  | 1726 | 1196 | 2922
| PEVF8 | 8" wide, front only | 92.8 | 0 | 92.8 | 1035 | 0 | 1035 |  | 1726 | 0 | 1726
| PEV10 | 10" wide | 118.6 | 82.6 | 201.2 | 1323 | 921 | 2245 |  | 2206 | 1536 | 3742
| PEVF10 | 10" wide, front only | 118.6 | 0 | 118.6 | 1323 | 0 | 1323 |  | 2206 | 0 | 2206
| PEV12 | 12" wide | 144.4 | 101 | 245.4 | 1611 | 1127 | 2738 |  | 2685 | 1878 | 4564
| PEVF12 | 12" wide, front only | 144.4 | 0 | 144.4 | 1611 | 0 | 1611 |  | 2685 | 0 | 2685
| Single PEV Finger |  |  |  | 5.7 | 63 |  |  |  | 106
Note: Door brackets and cable slack spools reduce cable capacity.
WMPV NetRunner™ Vertical Cable Managers | WMPV22E | 4.9" wide, 22RU | 17.3 | 17.3 | 34.6 | 193 | 193 | 386 |  | 321 | 321 | 643
| WMPVF22E | 4.9" wide, 22RU, front only | 17.3 | 0 | 17.3 | 193 | 0 | 193 |  | 321 | 0 | 321
| WMPV45E | 4.9" wide, 45RU | 17.3 | 17.3 | 34.6 | 193 | 193 | 386 |  | 321 | 321 | 643
| WMPVF45E | 4.9" wide, 45RU, front only | 17.3 | 0 | 17.3 | 193 | 0 | 193 |  | 321 | 0 | 321
| WMPVHC45E | 6.7" wide, 45RU | 30.7 | 30.7 | 61.4 | 342 | 342 | 685 |  | 571 | 571 | 1142
| WMPVHCF45E | 6.7" wide, 45RU, front only | 30.7 | 0 | 30.7 | 342 | 0 | 342 |  | 571 | 0 | 571
| Single WMPV Finger |  |  |  | 3.7 | 41 |  |  |  | 68
| Single WMPVHC Finger |  |  |  | 4.7 | 52 |  |  |  | 87
NRV NetRunner™ High Capacity Vertical Cable Managers | NRV6 | 6.7" wide, 45RU | 30.7 | 30.7 | 61.4 | 342 | 342 | 685 |  | 571 | 571 | 1142
| NRVF6 | 6.7" wide, 45RU, front only | 30.7 | 0 | 30.7 | 342 | 0 | 342 |  | 571 | 0 | 571
| NRV10 | 10" wide, 45RU | 49.1 | 49.1 | 98.2 | 547 | 547 | 1095 |  | 913 | 913 | 1826
| NRVF10 | 10" wide, 45RU, front only | 49.1 | 0 | 49.1 | 547 | 0 | 547 |  | 913 | 0 | 913
| NRV12 | 12" wide, 45RU | 60.7 | 60.7 | 121.4 | 677 | 677 | 1354 |  | 1129 | 1129 | 2258
| NRVF12 | 12" wide, 45RU, front only | 60.7 | 0 | 60.7 | 677 | 0 | 677 |  | 1129 | 0 | 1129
| Single NRV Finger |  |  |  | 4.7 | 52 |  |  |  | 87
WMP PatchLink™ Horizontal Cable Managers | WMP1E | 2RU, front/rear | 7.6 | 10.6 | 18.2 | 84 | 118 | 203 |  | 141 | 197 | 338
| WMPF1E | 2RU, front only | 7.6 | 0 | 7.6 | 84 | 0 | 84 |  | 141 | 0 | 141
| WMPH2E | 2RU, front/rear, w/ bend rad. clips | 5.9 | 10.6 | 16.5 | 65 | 118 | 184 |  | 109 | 197 | 306
| WMPHF2E | 2RU, front only, w/ bend rad. clips | 5.9 | 0 | 5.9 | 65 | 0 | 65 |  | 109 | 0 | 109
| WMPSE | 1RU, front/rear | 3.5 | 6.3 | 9.8 | 39 | 70 | 109 |  | 65 | 117 | 182
| WMPFSE | 1RU, front only | 3.5 | 0 | 3.5 | 39 | 0 | 39 |  | 65 | 0 | 65
| WMPLSE | 1RU, front/rear, short depth | 2.1 | 6.3 | 8.4 | 23 | 70 | 93 |  | 39 | 117 | 156
| WMPLFSE | 1RU, front only, short depth | 2.1 | 0 | 2.1 | 23 | 0 | 23 |  | 39 | 0 | 39
Note: Rear section may be partially blocked by rack posts
NCMH NetManager™ Horizontal Cable Managers | NCMH2 | 2RU, front/rear | 6 | 8 | 14 | 66 | 89 | 156 |  | 111 | 148 | 260
| NCMHF2 | 2RU, front only | 6 | 0 | 6 | 66 | 0 | 66 |  | 111 | 0 | 111
| NCMHF1 | 1RU, front only | 2.3 | 0 | 2.3 | 25 | 0 | 25 |  | 42 | 0 | 42
NM NetManager™ High Capacity Horizontal Cable Managers | NM1 | 1RU, front/rear | 3.3 | 4.1 | 7.4 | 36 | 45 | 82 |  | 61 | 76 | 137
| NMF1 | 1RU, front only | 3.3 | 0 | 3.3 | 36 | 0 | 36 |  | 61 | 0 | 61
| NM2 | 2RU, front/rear | 9.8 | 11.1 | 20.9 | 109 | 123 | 233 |  | 182 | 206 | 388
| NMF2 | 2RU, front only | 9.8 | 0 | 9.8 | 109 | 0 | 109 |  | 182 | 0 | 182
| NM3 | 3RU, front/rear | 17.3 | 22 | 39.3 | 193 | 245 | 438 |  | 321 | 409 | 731
| NMF3 | 3RU, front only | 17.3 | 0 | 17.3 | 193 | 0 | 193 |  | 321 | 0 | 321
| NM4 | 4RU, front/rear | 24.3 | 31.9 | 56.2 | 271 | 356 | 627 |  | 452 | 593 | 1045
| NMF4 | 4RU, front only | 24.3 | 0 | 24.3 | 271 | 0 | 271 |  | 452 | 0 | 452
Note: Rear section may be partially blocked by rack posts
CMPH Open-Access™ Horizontal Cable Managers | CMPH1 | 1RU, front/rear | 2.3 | 2.9 | 5.2 | 25 | 32 | 58 |  | 42 | 53 | 96
| CMPHF1 | 1RU, front only | 2.3 | 0 | 2.3 | 25 | 0 | 25 |  | 42 | 0 | 42
| CMPH2 | 2RU, front/rear | 5.3 | 10.8 | 16.1 | 59 | 120 | 179 |  | 98 | 200 | 299
| CMPHF2 | 2RU, front only | 5.3 | 0 | 5.3 | 59 | 0 | 59 |  | 98 | 0 | 98
| CMPHH2 | 2RU, front only, larger D-rings | 10.8 | 0 | 10.8 | 120 | 0 | 120 |  | 200 | 0 | 200
| CMPHHF1 | 1RU, front only, larger D-rings | 2.9 | 0 | 2.9 | 32 | 0 | 32 |  | 53 | 0 | 53
Note: Rear section may be partially blocked by rack posts
PEHF PatchRunner™ High Capacity Horizontal Cable Managers | PEHF2 | 2RU, front only | 16.6 | 0 | 16.6 | 185 | 0 | 185 |  | 308 | 0 | 308
| PEHF3 | 3RU, front only | 29.6 | 0 | 29.6 | 330 | 0 | 330 |  | 550 | 0 | 550
| PEHF4 | 4RU, front only | 42.8 | 0 | 42.8 | 477 | 0 | 477 |  | 796 | 0 | 796
CMVDR Vertical D-rings | CMVDR1 | 5.70"L x 2.00"W |  |  | 6 |  |  | 66 |  |  |  | 111
| CMVDR1S | 3.30"L x 2.00"W |  |  | 3 |  |  | 33 |  |  |  | 55
| CMVDR2 | 5.70"L x 3.00"W |  |  | 10.8 |  |  | 120 |  |  |  | 200
| CMVDR2S | 3.30"L x 3.00"W |  |  | 6 |  |  | 66 |  |  |  | 111
| CMVDRC | between-racks, 5.60"L x 8.00"W |  |  | 24 |  |  | 267 |  |  |  | 446
CM Cable Routing Troughs | CMLT19 | lower trough w/ bend radius |  |  | 22.7 |  |  | 253 |  |  |  | 422
| CMUT19 | upper trough w/ bend radius |  |  | 8.2 |  |  | 91 |  |  |  | 152
| CMT4 | horizontal trough |  |  | 21.9 |  |  | 244 |  |  |  | 407
*Capacity is calculated for within the trough channel only. Higher capacities can be achieved when cables are tied together.
CWMPV IN-Cabinet Vertical Cable Manager | CWMPV2418 | side mount, 2"W x 4"D x 2.6'H | 5.7 | 0 | 5.7 | 63 | 0 | 63 |  | 106 | 0 | 106
| CWMPV3418 | side mount, 3"W x 4"D x 2.6'H | 9.1 | 0 | 9.1 | 101 | 0 | 101 |  | 169 | 0 | 169
| CWMPV2440 | side mount, 2"W x 4"D x 6'H | 5.7 | 0 | 5.7 | 63 | 0 | 63 |  | 106 | 0 | 106
| CWMPV3440 | side mount, 3"W x 4"D x 6'H | 9.1 | 0 | 9.1 | 101 | 0 | 101 |  | 169 | 0 | 169
| CWMPV2318 | side mount, 2"W x 3"D x 2.6'H | 5.2 | 0 | 5.2 | 58 | 0 | 58 |  | 96 | 0 | 96
| CWMPV3318 | side mount, 3"W x 3"D x 2.6'H | 7.8 | 0 | 7.8 | 87 | 0 | 87 |  | 145 | 0 | 145
| CWMPV2340 | side mount, 2"W x 3"D x 6'H | 5.2 | 0 | 5.2 | 58 | 0 | 58 |  | 96 | 0 | 96
| CWMPV3340 | side mount, 3"W x 3"D x 6'H | 7.8 | 0 | 7.8 | 87 | 0 | 87 |  | 145 | 0 | 145
J-PRO & J-MOD J Hooks | JP75^ | J-Pro™ cable support, 0.75" |  |  | 0.626 |  |  | 11 |  |  |  | 16
| JP131^ | J-Pro™ cable support, 1.31" |  |  | 1.74 |  |  | 32 |  |  |  | 45
| JP2^ | J-Pro™ cable support, 2.0" |  |  | 3.155 |  |  | 58 |  |  |  | 82
| JP4^ | J-Pro™ cable support, 4.0" |  |  | 13.478 |  |  | 250 |  |  |  | 350
| JMJH2^ | J-Mod™ cable support, 2.0" |  |  | 3.037 |  |  | 56 |  |  |  | 79
*Capacity is calculated for J Hooks with a 50% recommended fill and 70% maximum fill.
Cable Capacity Calculator

## numbers (hidden)
in. | no
mm | yes
30% | 50%
50% | 70%
0.215 | 0.185 | 0.275 | 0.15 | 0.235